## Flow
Computing the Flow Rate: US GPM
flowRate = Cv*sqrt(dP/d) * Cturns * Ce * Cp
| Cv: | Some strange function of CBV
| CBV: | Pipe size (inches)
| dp: | Differential Pressure (psi)
Or in (ft) by multiplying by 2.31
| d: | Density of water at 60F (16C) is 1
or (LB/Ft^3) by multiplying by 62.4
Should we bring in temperurature?
| Ce: | Constant adjustment for Ethylene. Strange function of E% and temp
| Cp: | Constant adjustment for Propylene. Strange function of P% and temp
| E%: | % Ethylene
| P%: | % Proplene

## Cv
Columns A=CBV and D=Cv are copied from the chart
Cv is too large. Hence, column C=ln(Cv) makes it smaller. We will learn this.
The function ln(Cv) = f( CBV ) is almost linear, but not quite
Hence, I computed column B = CBV^2
Then I did regression to learn ln(Cv) = b + c1 CBV + c2 CBV^2
Column F = ln(Cv) gives the approximate values.
Column G says that each is 2% accorate. Is that good enough?
See plot below
Column H is the approximate Cv
CBV | CBV^2 | ln(Cv) | Cv |  | ln(Cv) |  | Cv
2 |  |  | 27.8979 |  | 4.1148 |  | 61.2412
2.5 | 6.25 | 4.2341 | 69 |  | 4.3352 | 0.02388 | 76.3415
3 | 9 | 4.5747 | 97 |  | 4.6477 | 0.015945 | 104.3401
4 | 16 | 5.5413 | 255 |  | 5.2331 | -0.055615 | 187.3703
5 | 25 | 5.7807 | 324 |  | 5.7659 | -0.0025639 | 319.2333
6 | 36 | 6.107 | 449 |  | 6.2462 | 0.022783 | 516.0283
8 | 64 | 7.0273 | 1127 |  | 7.0489 | 0.003065 | 1151.5371
10 | 100 | 7.6256 | 2050 |  | 7.6412 | 0.0020412 | 2082.1594
12 | 144 | 8.0504 | 3135 |  | 8.0231 | -0.0033911 | 3050.5743
| Coefficients | Standard Error | t Stat | P-value | Lower 95% |  | Upper 95% | Lower 95.0% | Upper 95.0%
Intercept | 2.5758 | 0.30234 | 8.5196 | 0.00036657 | 1.7986 |  | 3.353 | 1.7986 | 3.353
X Variable 1 | 0.76952 | 0.099541 | 7.7307 | 0.00057856 | 0.51364 |  | 1.0254 | 0.51364 | 1.0254
X Variable 2 | -0.026298 | 0.0068699 | -3.828 | 0.012272 | -0.043957 |  | -0.0086384 | -0.043957 | -0.0086384
CBV | ln(CV) | ln(CV)
2.5 | 4.2341 | 4.3352
3 | 4.5747 | 4.6477
4 | 5.5413 | 5.2331
5 | 5.7807 | 5.7659
6 | 6.107 | 6.2462
8 | 7.0273 | 7.0489
10 | 7.6256 | 7.6412
12 | 8.0504 | 8.0231

## Cv 2
| For pipe size (2in), set Cv = |  | 27.8979
Let's try to compute Cv when CBV size is 2 inchs.
dp (ft) | 0.1
dp (pst) | 0.04329
flow | 5.8045
Cv | 27.8979 | plugging this in to the ap gives the right answer
Our Cv | 61.2412 | So it is not so close

## turn 1
Turn
|  | cm Bot | Flow b | Approx
| 0 |  |  | 0.36
1 | 0.5 | -2.9 | 0.9 | 0.9 | b | 0.36
|  | 0 | 1 |  | m | 1.08
2 | 1 | 5.7 | 1.2625 | 1.44
3 | 1.5 | 16 | 1.9239 | 1.98
4 | 2 | 24.5 | 2.7238 | 2.52
5 | 2.5 | 30 | 3.4108 | 3.06
6 | 3 | 34.5 | 4.1 | 3.6
7 | 3.5 | 37.5 | 4.6353 | 4.14
8 | 4 | 39.8 | 5.0925 | 4.68
9 | 4.5 | 41.5 | 5.4591 | 5.22
10 | 5 | 43 | 5.8045 | 5.76
|  | 43.7 | 6
|  | 56.3 | 10
|  | 112.6 | 100
Turn
| 0 |  | 0.36
| 0.5 | 0.9 | 0.9
| 1 | 1.2625 | 1.44
| 1.5 | 1.9239 | 1.98
| 2 | 2.7238 | 2.52
| 2.5 | 3.4108 | 3.06
| 3 | 4.1 | 3.6
| 3.5 | 4.6353 | 4.14
| 4 | 5.0925 | 4.68
| 4.5 | 5.4591 | 5.22
| 5 | 5.8045 | 5.76

## turn 2
The right most line is for 5 turns, i.e. 100% open.
The left most line is for 0.5 turns, i.e. 0.5/5 = 10% open.
When head, ie differential pressure, is 0.1, ie bottom
Flow decreases from 6 to 0.9, ie decreases by a factor of ~1/6. Set Cturn=1/6.
When head, ie differential pressure, is 300, i.e. top
Flow decreases from 300 to 50, ie decreases by a factor of ~1/6. Set Cturn=1/6.
This argues that we multiply Flow by Cturn.

## turn
Turn | Flow | Approx
0 | 0.9 | 0
0.5 | 0.9 | 0.58
1 | 1.2625 | 1.16
1.5 | 1.9239 | 1.74
2 | 2.7238 | 2.32
2.5 | 3.4108 | 2.9
3 | 4.1 | 3.48
3.5 | 4.6353 | 4.06
4 | 5.0925 | 4.64
4.5 | 5.4591 | 5.22
5 | 5.8045 | 5.8

## Ce
%e / C | 4.5 | 21 | 82
0 | 1 | 1 | 1.01
10 | 0.99 | 0.99 | 1.01
20 | 0.99 | 0.99 | 1
30 | 0.98 | 0.98 | 1
40 | 0.97 | 0.97 | 0.98
50 | 0.96 | 0.96 | 0.97
C<=21 | Ce0 = Ce(%e=0) = |  | 1
| Ce50 = Ce(%e=50) = |  | 0.96
C>=21 | Ce0 = Ce(%e=0) = |  | 1.0 + (1.01-1.0)/(82-21) * (C-21) | y = y1 + (y2-y1)/(x2-x1) * (x-x1)
| Ce50 = Ce(%e=50) = |  | 0.96 + (0.98-0.96)/(82-21) * (C-21)
Ce = Ce0 + (Ce50-Ce0)/50 * %e

## Cp
%p / C | 4.5 | 21 | 82
0 | 1 | 1 | 1.01
10 | 0.99 | 0.99 | 1.01
20 | 0.99 | 0.99 | 1.01
30 | 0.99 | 0.99 | 1.01
40 | 0.98 | 0.98 | 1
50 | 0.97 | 0.98 | 1
C<=21 | Cp0 = Cp(%p=0) = |  | 1
| Cp50 = Cp(%p=50) = |  | 0.97 + (0.98-0.97)/(21-4.5) * (C-4.5)
C>=21 | Cp0 = Cp(%p=0) = |  | 1.0 + (1.01-1.0)/(82-21) * (C-21) | y = y1 + (y2-y1)/(x2-x1) * (x-x1)
| Cp50 = Cp(%p=50) = |  | 0.98 + (1-0.98)/(82-21) * (C-21)
Cp = Cp0 + (Cp50-Cp0)/50 * %p

## Sheet4
Flow | 6.84
Head | 0.1
Turn | 6
r | 0.0021374
Head 0 | 0.1
Flow 0 | 6.84
m | 1.08
b | 0.36

## Sheet5
Minimum flow
Model CBV |  | 1ft presure drop
pipe size | Cv Fully | 50% open
inches | open | GPM
2.5 | 69 | 18
3 | 97 | 19
4 | 255 | 46
5 | 324 | 60
6 | 449 | 100
8 | 1127 | 307
10 | 2050 | 559
12 | 3135 | 1532